# Activity: Building Design and Protective Barriers – ANSWER KEY

- List some factors that need to be taken into consideration when designing an x-ray room or department.

Location

Protective barriers

Use of adjoining rooms

- What types of radiation do we need to protect against

- Primary radiation

- Scatter radiation*

- Leakage radiation*

*Both scatter & leakage radiations are collectively known as secondary radiation

- Define & describe the 7 factors needed to be taken in consideration when determining the shielding necessary in diagnostic x-ray installations?

- Primary or Secondary Barriers

Primary

Any wall to which a useful beam may be directed

Materials- Lead bonded to drywall or wood paneling

Concrete, concrete block or brick

4” of masonry is equivalent to 1/16” of lead

Secondary

Less thick than primary barriers

Materials- Lead often not required

4 x 5/8” drywall

For control booth, 4 thicknesses of drywall and ½” plate glass often all that is needed

- Distance from the radiation source

Distance between the nearest point of area to be shielded & main position of the tube

To adjacent room occupied not just to inside wall of x-ray room

Often best to put tube in the middle of the room,

If positioned close to the wall, extra care to protect from leakage

- Occupancy factor of the area (T)

Use of the area to be protected

High use area more shielding needed than if low use area

Time of occupancy (T) the determining factor

| Complete the Occupancy Factors as per SC 35 |  |
| --- | --- |
| T = 1 | Administrative offices and receptionist areas, laboratories, pharmacies and other areas fully occupied by an individual, attended waiting rooms, children’s indoor play areas, adjacent X-ray control room, living quarter |
| T = 1/2 | Rooms used for patient examinations and treatments |
| T = 1/5 | Corridors, patient rooms, staff lounges, staff rest rooms |
| T = 1/8 | Corridor doors |
| T = 1/20 | Public toilets, unattended vending areas, storage rooms, outdoor areas with seating, unattended waiting rooms, patient holding areas |
| T = 1/40 | Outdoor areas with only transient pedestrian or vehicular traffic, unattended parking lots, vehicular drop off areas (unattended), attics, stairways, unattended elevators, janitor’s closets |

- Controlled or Uncontrolled area

Controlled

Hospital area occupied by workers who have been trained in radiation safety procedures & who wear radiation monitoring devices

Uncontrolled

Area in which member of the general public may be found

Individuals who are not trained to work with radiation

- Workload (W)

Level of radiation activity in a room per week

Greater workload (activity) means more shielding needed

W is expressed in mA minutes per week

- Maximum & average tube potential & output

KVp is used to measure penetrability

Can go as high as 150 kVp, but mostly around 75 kVp

Constant operation assumed at higher kVp to be safe

- Use factor (U)

Amount of time the useful beam is directed towards is particular barrier

| Complete the Use Factors as per SC 35 |  |
| --- | --- |
| Primary Barrier |  |
| U = 1 | Floors of radiation rooms, walls containing a vertical image receptor; any other walls, doors, or ceiling areas routinely exposed to the direct radiation beam |
| U = 1/4 | Doors and wall areas of radiation rooms not routinely exposed to the direct radiation beam |
| U = 1/16 | Ceiling areas of radiation rooms not routinely exposed to the direct radiation beam |
| Secondary Barrier |  |
| U = 1 | The use factor for secondary protective barriers is always taken to be 1 |